Duo-Gard Industries Inc.

40442 Koppernick Road

Canton, Michigan  48187

Phone    (734) 207-9700

Fax    (734) 207-7995

www.duo-gard.com

SECTION 08 62 13

Unit Skylights

# Maximizer Skylight

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Self flashing skylight.

B.	Curb mounted skylight.

  - RELATED SECTIONS

- Section 07 60 00 Flashing and Sheet Metal.

- Section 07 92 00 Joint Sealants.

- Section 08 80 00 Glazing.

1.3	REFERENCES

A.	ASTM D 635 - Rate of Burning and/or Extent and Time of Burning of Self-Supporting Plastics in a Horizontal Position.

B.	ASTM D 638 – Standard Test Method for Tensile Properties of Plastics.

C.	ASTM D 790 – Standard Test Method for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

D.	ASTM D 1929 – Ignition Temperature of Plastics.

E.	ASTM D 2843 – Density of Smoke.

F.	NFRC 100 – U-Factor.

G.	NFRC 200 – Solar Heating Gain Coefficient.

H.	NFRC 500 – Condensation.

1.4	DESIGN REQUIREMENTS

A.	Basic Wind Speed: 90 mph. (If alternate loading is required please contact Duo-Gard).

- Exposure Category: designed to required category, contact Duo-Gard.

- Maximum Allowable Deflection of Structural Members:  Maximum of L/120 of clear span.

- Maximum Allowable Deflection of Polycarbonate Structured Sheet:  Maximum of 1 inch.

1.5	SUBMITTALS

A.	Comply with Section 01 33 00 - Submittal Procedures.

B.	Product Data:  Submit manufacturer's product data, including materials, components, fabrication, finish, and installation instructions.

C.	Shop Drawings:  Submit manufacturer's shop drawings, including plans, elevations, sections, and details, indicating dimensions, tolerances, profiles, anchorage, connections, fasteners, hardware, provisions for expansion and contraction, drainage, flashing, finish, and attachments to supports of glazing, framing, and options.

D.	Samples:  Submit manufacturer’s samples for each glazing type, framing system, finish, and color specified.

E.	Manufacturer’s Certification:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

F.	Manufacturer’s Project References:  Submit list of completed projects including project name and location, name of architect, and type of daylighting manufactured.

- Warranty:  Submit manufacturer's standard warranty.

- Testing Reports:  Submit manufacturer’s test reports.

  - Fire tests.

  - Air infiltration test.

  - Water penetration test.

1.6	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:

1.	Continuously engaged in translucent insulated daylighting manufacturing with a minimum of 10 years successful experience.

2.	Able to demonstrate successful performance on comparable projects.

3.	Responsible for all components, including structural design.

- Installer’s Qualifications:

1.	Authorized by manufacturer to install translucent glazing products.

2.	Trained by manufacturer’s standard training methods and policies.

C.	  Approved Manufacturers:

All manufacturers acceptable for use on this project must be approved prior to bid. Manufacturers must submit evidence of compliance with all performance criteria specified including test reports.  Any exceptions taken from this specification must be noted on the approval request.  If approval is given, product performance will be as specified.  Should non-compliance be subsequently discovered, the previously given approval will be invalidated and use of the product on the project will be disallowed.  Requests for approval, with all appropriate submittal data and samples must be received no less than 15 days prior to bid date.  A list of all approved manufacturers and products will be issued by addendum. No other manufacturers will be acceptable. No verbal approval will be given.

1.7	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to the site in manufacturer's original, unopened containers and packaging, with labels clearly identifying product name, manufacturer, and location of installation.

B.	Storage:

1.	Store materials in a clean, dry area indoors in accordance with manufacturer's instructions.

2.	Keep temporary protective liners in place.

3.	Do not expose panels to direct sunlight for extended periods.

C.	Handling:  Handle materials and products in strict compliance with manufacturer’s instructions and recommendations.

1.	Exercise caution when hoisting units to the roof so as not to scratch, bend or damage.

2.	Do not store skylights with the temporary protective liners in the sun.  Remove temporary protective liners as recommended by manufacturer.

  - WARRANTY

A.	Warranty Period:  Ten years on weatherization starting on date of substantial completion.

PART 2	PRODUCTS

2.1	MANUFACTURER

- Duo-Gard Industries Inc., 40442 Koppernick Road, Canton, Michigan 48187.

Phone (734) 207-9700.  Fax (734) 207-7995.  Web Site:  www.duo-gard.com.

2.2	CURB MOUNTED SKYLIGHTS

- Description:

A self flashing curb mounted, factory assembled, glazed fenestration unit skylight integrating up to three energy-saving, light transmitting technologies to achieve top performance in translucent daylighting.

- Standard Sizes:

- 4’-0” x 4’-0”

- 4’-0” x 8’-0”

C.	Glazing Selections:

1.	Model M1, Single Polycarbonate Dome Only.

a.	Polycarbonate dome color – Clear.

b.	Polycarbonate dome thickness - 1/8 inch (3mm).

c.	Light transmittance – 83%

d.	SHGC – 0.96

e.	U-value – 1.17

2.	Model M16, Single Polycarbonate Dome with Diffusion Panel.

a.	Polycarbonate dome color – Clear.

b.	Polycarbonate dome thickness - 1/8 inch (3mm).

c.	Diffusion panel color – Clear.

d.	Diffusion panel thickness – 16mm.

e.	Light transmittance – 62%

f.	SHGC – 0.65

g.	U-value – 0.30

3.	Model M160, Single Polycarbonate Dome with Insulated Diffusion Panel.

a.	Polycarbonate dome color – Clear.

b.	Polycarbonate dome thickness - 1/8 inch (3mm).

c.	Diffusion panel color – Clear.

d.	Diffusion panel thickness – 16mm.

e.	Insulation - Lumira®.

f.	Light transmittance – 52%

g.	SHGC – 0.59

h.	U-value – 0.18

D.	Frame finish:  Clear Anodized (other colors available, please contact Duo-Gard).

E.	Fire Tests:

- Smoke Developed, ASTM D 635:  CC1.

- Ignition Temperature, ASTM D1929.

- Density of Smoke, ASTM D 2843.

2.3	MATERIALS

A.	Glazing:

1.	Dome:  Polycarbonate.

2.	Diffusion Panel:  Polycarbonate structured sheet.

3.	Polycarbonate UV Stabilization:  Coextruded into panels, not coated.

4.	Resist Yellowing:  Maximum 10 delta for a minimum of 10 years.

5.	Sheet Appearance:  Uniform in color.

6.	Expansion and Contraction:  Design and install components with provisions for expansion and contraction based on geographical location.

7.	Gaskets and Dry Seals:  Butyl tape and TPV (Santoprene).

B.	Joint Sealant:

1.	Factory-Applied Sealant:  Gunnable, nonhardening, elastomeric sealant.

ASTM C 920, Type S, Class 12, Grade NS.  Fed Spec TT-S-1657, Type 1.n.

2.	Field-Applied Sealant:  Approved by translucent insulated daylighting manufacturer.  As specified elsewhere in specifications.

C.	Field Fasteners:

1.	Comply with translucent insulated daylighting manufacturer’s instructions for fastener types, quantities, and usage.

- Chromate-plated, zinc or stainless steel.  Prevent oxidation or electrolytic interaction with framing.

3.	Aluminum-to-Aluminum Connections:  Self-drilling screws, size and length for full-thread engagement, as determined by manufacturer.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive unit skylight.  Notify Architect of conditions that would adversely affect installation or subsequent utilization of daylighting.  Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	PREPARATION

- Ensure supports to receive unit skylight are clean, flat, level, plumb, square, accurately

aligned, and correctly located.

3.3	INSTALLATION

A.	Install unit skylight in accordance with manufacturer's instructions at locations indicated on the drawings.

B.	Install unit skylight level, plumb, square, accurately aligned, correctly located, and without warp.

C.	Anchor unit skylight securely in place to supports.  Use attachment methods permitting adjustment for construction tolerances, irregularities, alignment, and expansion and contraction.

D.	Install unit skylight including fasteners, hardware, gaskets, joint sealants, and glazing materials required for a complete, weathertight installation.

E.	Joint Sealants:  Install joint sealants as specified elsewhere in specifications.

F.	Repair minor damages to metal finish or glazing in accordance with manufacturer's instructions and as approved by Architect.  Remove and replace damaged components that cannot be successfully repaired as determined by Architect.

3.4 	CLEANING

A.	Clean unit skylight in accordance with manufacturer's instructions.

B.	Clean inside and outside of unit skylight immediately after installation and after joint sealants have cured.

C.	Remove temporary protective liners at time of installation (interior) and after installation is complete (exterior).

D.	Remove excess joint sealant in accordance with sealant manufacturer's instructions.

E.	Do not use harsh cleaning materials or methods that would damage metal finish, acrylic dome or polycarbonate structured sheet.

3.5	PROTECTION

A.	Protect installed unit skylight from damage during construction.

B.	Remove and replace damaged unit skylight components as determined by Architect.

END OF SECTION